LTEB DISPLAY – how to program and change 

To change any parameter – eg maximum speed P01 (SEE VIEW OF SCREEN BELOW)
1.	From STOP mode Hold the ‘Hex’ key for 2 seconds.  P-1 or P-0 etc  should show
2.	Use the arrow keys to toggle to desired parameter e.g. P01 (= max speed). 
3.	Press hex key (single press – 1 sec max) once to see the value
4.	Adjust as required using up down arrows.
5.	Press the hex key once to save.
6.	To exit programming mode and go back to the main screen Hold the ‘Hex’ key for 2 seconds.  

To check the VSD speed in hertz (or to check amperage or kilowatts power consumed)
-	whilst the VSD is running (and showing a speed) press the hex key with a single press (less than one second) you will then toggle through each of the following
1.	A  = current amperage 
2.	P =  current power consumption and kilowatts
3.	H = equals current speed in hertz
4.	No prefix - =  RPM rate as programmed in parameter P 10